Access Control and Security Management Software

Architectural and Engineering Specifications

TABLE OF CONTENTS

PART I	 GENERAL	4

1.1	GENERAL DESCRIPTION	4

1.2	SUBMITTALS	4

1.2.A	Shop Drawings	4

1.2.B	Product Data	5

1.2.C	As-Built Drawings	5

1.2.D	Manuals	5

1.3	QUALITY ASSURANCE	7

1.3.A	Manufacturer Qualifications	7

1.3.B	Contractor / Integrator Qualifications	7

1.3.C	Testing Agencies	7

1.4	WARRANTY	8

PART II	 PRODUCTS	9

2.1	MANUFACTURERS	9

2.2	DESCRIPTION	9

2.3	PERFORMANCE - MONITORING	10

2.3.A	Monitoring Mode	10

2.3.B	Graphics Screen	12

2.3.C	Communication Methods	12

2.4	PERFORMANCE – PROGRAMMING & CONFIGURATION	13

2.4.A	User Section	13

2.4.B	Video Section	16

2.4.C	Definition Section	18

2.4.D	Devices Section	20

2.4.E	Alarm Interface	20

2.4 F 	Intrusion Integration	20

2.4.G	System Section	21

2.4.H	Report Section	21

2.4.I	Help Section	22

2.4.J	Options Section	23

2.4.K	System Status Section	23

2.4.L	Various Tools	23

2.4.M	Video Vault	23

2.5	PERFORMANCE – EntraPass Web / MOBILE APP	24

2.5.A	EntraPass Web	24

2.5.B	Mobile APP	29

2.6	INTEGRATION	30

2.6.A	SmartLink	30

2.6.B	Card Gateway	30

2.7	REDUNDANCY & MIRRORING	30

2.7.A	Redundant Server	30

2.8	SOFTWARE AUTO-UPDATER	31

2.9	HSPD-12 COMPLIANCE AND INTEGRATION	31

2.10	OPERATION	32

2.12	EQUIPMENT	36

2.12.A	Server and Redundant Server Requirements	36

2.12.B	Multi-Site Gateway Requirements	36

2.12.C Workstation Requirements	37

2.12.D	Controllers	37

2.12.E	KTES (Kantech Telephone Entry System)	38

2.12.F	Card and Reader Support	39

PART III	EXECUTION	40

3.1	TESTING	40

3.2	TRAINING	40

3.3	MAINTENANCE	40

- PART I		GENERAL

  - GENERAL DESCRIPTION

The Security Management System (SMS) shall be a modular secure access management system used to better control employee and visitor movements at various establishments. The SMS shall be designed to maximize all tools offered by the Windows platform. All commands shall be accessible using nothing more than a mouse, and keyboard use shall be limited to documenting fields requiring numeric or alphanumeric data.

The operating program shall be multi-user and multi-tasking and capable of running on a non-proprietary CPU or virtual machines. The application software shall be based on a standard, high level programming language. The SMS shall be modular to facilitate its installation and the development of its capabilities while avoiding major modifications in its operation and in saving all defined system and historical data.

The server shall be a database server using a Sybase embedded SQL database. All database management tools shall be included, such as back-up, indexing, and database cleaning tools. No third party database tools or licensing shall be required. The multi-site gateway shall communicate system information between the server and controllers. The workstations shall be the primary user interface to perform supervisory and programming functions.

The SMS shall enable the selection of at least two user languages. The basic dictionary shall include English, French, Spanish, Italian, Portuguese, Simplified Chinese, Dutch, Turkish, and German, however, the system shall include a vocabulary editor to be used in designing custom language dictionaries. The operator’s profile shall permit the selection of one of the two basic languages.

The SMS shall include RS-232 / RS-485 communication link between the various system components as well as TCP/IP network interface capability. Field devices such as card readers, alarm inputs, control points, etc. shall be connected to fully distributed intelligent field panels capable of operating without host computer intervention in a non-degraded mode.

The SMS shall be able to design customized ID cards directly from the access management software. No specific program or software other than the access management software and no additional licensing shall be required for this function. Any workstation shall be capable of being used as a badging station. Badging shall be fully integrated with the card database.

  - SUBMITTALS

- 1.2.A	Shop Drawings

Prior to assembling or installing the SMS, the Contractor shall provide complete shop drawings which include the following:

- Architectural floor plans indicating all system device locations.

- Full schematic wiring information for all devices. Wiring information shall include cable type, cable length, conductor routings, quantities, and point-to-point termination schedules.

- Complete access control system one-line block diagram.

- Statement of the system sequence of operation.

- Riser diagrams showing interconnections.

- Detail drawings showing installation and mounting.

- Fabrication drawings for console arrangements and equipment layout.

- Test and Commission site report

All drawings shall be fully dimensioned and prepared in DWG format using AutoCAD.

- 1.2.B	Product Data

Prior to assembling or installing the SMS, the Contractor shall provide the following:

- Complete product data and technical specification data sheets that includes manufacturer’s data for all material and equipment, including terminal devices, local processors, computer equipment, access cards, and any other equipment provided as part of the SMS.

- A system description, including analysis and calculations used in sizing equipment required by the SMS. The description shall show how the equipment operates as a system to meet the performance requirements of the SMS. The following information shall be supplied as a minimum:

- Central processor configuration and memory size.

- Description of site equipment and its configuration.

- Protocol description.

- Hard disk system size and configuration.

- Backup/archive system size and configuration.

- Startup operations.

- System expansion capability and method of implementation.

- System power requirements and UPS sizing.

- A description of the operating system and application software.

- 1.2.C	As-Built Drawings

At the conclusion of the project, the Contractor shall provide “as built” drawings. The “as built” drawings shall be a continuation of the Contractors shop drawings as modified, augmented, and reviewed during the installation, check out and acceptance phases of the project. All drawings shall be fully dimensioned and prepared in DWG format using AutoCAD.

- 1.2.D	Manuals

At the conclusion of the project, the Contractor shall provide copies of the manuals as described herein. Each manual’s contents shall be identified on the cover. The manual shall include names, addresses, and telephone numbers of each security system integrator installing equipment and systems and the nearest service representatives for each item of equipment for each system. The manuals shall have a table of contents and labeled sections. The manuals shall include all modifications made during installation, checkout, and acceptance. Date of project commencement, milestones, CCO’s and completion to be included also.  The manuals shall contain the following:

- Functional Design Manual

The functional design manual shall identify the operational requirements for the system and explain the theory of operation, design philosophy, and specific functions. A description of hardware and software functions, interfaces, and requirements shall be included for all system operating modes.  All operational changes required by customer are to be documented in writing where they differ from original Specification

- Hardware Manual

The hardware manual shall describe all equipment furnished including:

- General description and specifications

- Installation and test and commission procedures

- Equipment layout and electrical schematics to the component level

- System layout drawings and schematics

- Alignment and calibration procedures

- Manufacturers repair parts list indicating sources of supply

- Load calculations of equipment operating at maximum load.

- Software Manual

The software manual shall describe the functions of all software and shall include all other information necessary to enable proper loading, testing, and operation. The manual shall include:

- Definition of terms and functions

- Use of system and applications software

- Initialization, startup, and shut down

- Alarm reports

- Reports generation

- Data base format and data entry requirements

- Directory of all disk files

- Operators Manual

The operator’s manual shall fully explain all procedures and instructions for the operation of the system including:

- Computers and peripherals

- System startup and shut down procedures

- Use of system, command, and applications software

- Recovery and restart procedures

- Graphic alarm presentation

- Use of report generator and generation of reports

- Data entry

- Operator commands

- Alarm messages and reprinting formats

- System access requirements

- Maintenance Manual

The maintenance manual shall include descriptions of maintenance for all equipment including inspection, periodic preventive maintenance, fault diagnosis, and repair or replacement of defective components.  Maintenance manual shall also include a list of recommended spares which are liable to be encountered as part of routine service procedures.

  - QUALITY ASSURANCE

- 1.3.A	Manufacturer Qualifications

The manufacturers of all hardware and software components employed in the SMS shall be established vendors to the access control/security monitoring industry for no less than five (5) years and shall have successfully implemented at least 5 systems of similar size and complexity.

- 1.3.B	Contractor / Integrator Qualifications

- The security system integrator shall have been regularly engaged in the installation and maintenance of integrated access control systems and have a proven track record with similar systems of the same size, scope, and complexity.

- The security system integrator shall supply information attesting to the fact that their firm is an authorized Kantech Corporate Dealer.

- The security system integrator shall supply information attesting to the fact that their installation and service technicians are competent factory trained and certified personnel capable of maintaining the system and providing reasonable service time.

- The security system integrator shall provide a minimum of three (3) references whose systems are of similar complexity and have been installed and maintained by the security system integrator in the last five (5) years.

- There shall be a local representative and factory authorized local service organization that shall carry a complete stock of parts and provide maintenance for these systems.

- 1.3.C	Testing Agencies

- The following hardware have been tested and listed by Underwriters Laboratories (UL) for UL 294 for Access Control System Units.

- KT-300.

- KT-400.

- IP link.

- P225W26.

- P225KPW26.

- P225XSF.

- P225KPXSF.

- P325W26.

- P325KPW26.

- P325XSF.

- P325KPXSF.

- KT-MOD-REL8.

- KT-MOD-INP16.

- KT-MOD-OUT16.

- KT-3LED-Plate.

- KTES.

- The hardware shall comply with the following regulatory requirements:

- FCC Part 15 Class A.

- FCC Part 15 Class B.

- FCC Part 68 (TIA968).

- ICES-003.

- CE.

- ECCN for AES 128 bit encryption for IP communication.

    - IP Link or KT-400 only.

- Government standards NISPOM 5-313 Automated Access Control Systems, DICD Annex F 2.3 Accept/Reject Threshold Criteria, JAFAN Annex D 2.3 Accept/Reject Threshold Criteria.

- The SMS shall support Americans with Disabilities Act (ADA) compliance in door and access operation.

  - WARRANTY

The Security Management System (SMS) shall be provided with a 12 month product warranty from date of registration. Software version updates shall be available for no charge during this warranty. The software media warranty shall be 90 days.

- PART II		PRODUCTS

- 2.1	MANUFACTURERS

The Security Management System (SMS) shall be the Kantech EntraPass Corporate Edition.

- 2.2	DESCRIPTION

The Security Management System (SMS) shall be an integrated system that utilizes a Sybase embedded SQL database for the storage and manipulation of related data. The SMS shall include a server with applications software, multi-site gateways for communication between the server and controllers, operator and administrator workstations with appropriate software, hard copy printers and secure backup media. The security field devices (readers, door position switches, REX, etc.) shall communicate with the field panels via a dedicated cable network. The field panels shall communicate to the server via a Fast Ethernet 10/100 TCP/IP network, RS-232/RS-485 connection, or dial-up modem.

The SMS shall allow for growth and scalability from a smaller system to a larger, high-end, or enterprise system. The SMS shall be modular in nature, allowing system capacities to be easily expanded without requiring major changes to system operation. All defined system data as well as historical information shall be maintained. Customizable user interfaces shall allow management of system information and activity for administrators and operators. The response time between the moment when a card is presented at the reader and when the door is unlocked shall not exceed one second. The SMS shall include a badging solution with a GUI for badge design. No extra licensing shall be required for the badging solution.

The SMS shall be able to connect to authenticated non-SSL or non-authenticated email server for all email features described.  The SMS shall be able to connect to SMTP or POP3 authenticated email server.

The SMS shall support up to:

20		Workstations

10		Concurrent Web/Mobile applications

20		Redundant servers

40		Digital video recorders

41		Multi-site gateways

17,408		Door controllers per Multi-site gateway

69,632		Card readers and/or keypads and/or elevator cabs of 64 floors each per 			Multi-site gateway

Unlimited	Access cards

Unlimited 	Card families or site codes

4,456,448	Monitored points per Multi-site gateway

4,456,448	Control relays per Multi-site gateway

2		Simultaneous operator languages

- 2.3	PERFORMANCE - MONITORING

- 2.3.A	Monitoring Mode

1.	The SMS shall enable every operator to customize their desktop configuration. It shall be possible to modify the desktop appearance and to create up to 8 desktops and to associate up to10 different display screens to each. It shall be possible to modify the size and position of all screens. It shall be possible to determine if these screens shall be floating anywhere on the desktop or fixed on the desktop. If the workstation is equipped with a dual output video card and two or more monitors, it shall be possible to distribute the screen to multiple monitors. However, each screen shall be able to be viewed alone or together depending on operator needs. Once these parameters are saved, the configuration shall automatically take effect whenever the operator logs in.

For all types of screens, it shall be possible to access the general properties of the screen by simply right clicking at the center of the screen. From there it shall allow for linkage between associated screens without having to exit the current screen or section. It shall be possible to right click events on the desktop for editing which shall bring the user directly to the card, door, or component window and back.

- Message Screen

All events that occur shall appear in real time. The text shall include at least the date, time, and a pertinent description of the event as well as its condition. The display of this screen shall be customizable and a different background and message color can be used for every type of event.

In addition the background color shall be chosen per operator.  Events shall appear in their defined color or the operator shall have the option to choose a text color for the events.

All component modification events shall be tagged with an addition (+), modification (=) or deletion (-) tag.

Every in-coming event shall be documented by one or more icons representing video images, photos, access card, server, gateway, controller, card reader, and relay or supervision point. It shall be possible to classify the events on the screen by sequence, date and time, type of event, or type of message. In addition, a text filter shall be available to facilitate searching. It shall be possible to access the last up to 100,000 transactions from this window without the need to request a special report.

It shall be possible to right click on an event and perform edit or other functions linked to the event.

3.	Card Holder Photo Screen

When a card is presented to a card reader, the software shall automatically display the photograph of the cardholder in this window. From this screen it shall be possible to select the cardholder’s name, card number, event text, and comments as well as specify a door or group of doors for which the operator would like to display a photo. The SMS shall support the display of up to 4 pictures simultaneously.  Furthermore the SMS shall allow that each picture box be assigned to a specific door for additional filtering

4.	Filtered Message Screen

This screen shall be a copy of the text messages screen except it shall be possible to select a specific message filter. The SMS shall include a choice of pre-configured filters and the ability to create customized filters. For every new filter it shall be possible to associate a name to it, select the type of event, select door, select workstation, select gateway, select supervision input, and select output.

5.	Alarm Screen

Alarms that require an acknowledgement by an operator shall be displayed on this screen in text form only. The text shall include at least the date, time and description of the alarm, and its condition. It shall be possible to classify events on the screen by sequence, date and time, type of event, or type of message. A text filter shall be available in order to facilitate the search.

If instructions about an alarm are envisaged, they shall automatically appear in a second window on the screen. If a graphic is associated with the alarm, it shall appear automatically on the screen defined to this effect. The icon associated to the control point shall be represented and show the actual state of the point.

The operator shall be able to access a log book in order to document the alarm that occurred. Once this information is recorded in the log it shall not be erasable or modifiable.  Operators shall also be able to see previous comments or system logs added for this event.

Operators shall be able to run a report of the alarms from this window.

It shall be possible to associate video call-up with an alarm. When this occurs, the main screen shall become the video screen, not the alarm screen.

6.	Video Screen (Video View)

When the SMS is integrated with American Dynamics or Panasonic DVR/NVR, it shall be possible to view the video images of cameras associated with them. The SMS shall enable the creation of an unlimited number of video views, each one associated with up to 16 different cameras or graphics. It shall be possible for the operator to see at a minimum 48 cameras simultaneously using three video views per screen. It shall be possible for an operator to edit or modify an existing view or create a new one directly from this screen. For each video view it shall be possible to select sequential, mosaic pattern, or preset viewing modes.

The SMS shall allow the operator to switch between pre-programmed video and dynamic view. The dynamic view shall allow the operator to select any camera and view it regardless of the need to create a new video view.  The dynamic view shall support up to 16 cameras simultaneously.

It shall be possible for an operator to access all the commands of a motion PTZ camera to include rotate on its axis, adjust its focus, and have a larger view of the image. Accessibility to camera images and commands shall be limited by operator security level.

No additional licensing shall be required to perform this function.

- Historical Message Screen

This screen shall allow operators to choose from a previously created custom report. Operators shall choose a start/end date/time.  The report will be populated in this window and have the same characteristics of the message screen including all right click functions.

The historical message screen shall allow operators to add comments to any event this can be later seen and reviewed.

- 2.3.B	Graphics Screen

1.	There are three options for graphics that appear as background on the screen. The first is a reproduction of the building(s) floor by floor. The graphic module shall be capable of importing files in BMP, EMF, WMF, JPEG, GIF, PCX, PNG, TIF, or PCD formats.

2.	The second option is using web pages, or WebViews, as background on the screen. This can be used in the following manners:

  - Accessing to DVR web servers.

  - Embedding default web pages into operator desktops.

  - Adding an IP camera onto a video view.

  - Embedding intranet pages or directories into the operator environment.

  - Adding PDF, Word documents, etc. to the desktop.

  - HTML or PDF pop-up instruction on alarm.

  - Integrating report folders in the desktop for quick access.

3.	The third option is to assign a live video view as background on the screen if video integration is being utilized.

4.	For all three options, control points shall be represented by a descriptive icon. Control points include workstations, gateways, controllers, card readers, doors equipped with either card readers or supervision contacts, cameras, relays, cameras, video views, task triggers and input monitoring points such as motion sensors. The icons shall be animated, meaning they shall represent the state of the point to which they are associated in real time. Every graphic shall support at least 100 control points.

Right clicking on an icon shall directly access the manual commands of each control point. A door shall be capable of but not limited to temporarily unlocking, manually unlocking or locking, and enabling or disabling a reader, viewing the reader’s comments, and enabling or disabling the KT-400 door contact. A supervision point shall be capable of being enabled or disabled. A control relay shall be capable of being activated, deactivated, or temporarily activated. Cameras shall be capable of viewing images or live video.

No additional licensing shall be required to perform this function.

- 2.3.C	Communication Methods

- The SMS shall ensure the communication to remote sites over a LAN or WAN/Internet using a dedicated communication server device, Kantech IP Link or the KT-400 controller. This shall only be applicable with the use of Multi-site Gateways. It shall ensure secure communications by the use of 128-bit AES Encryption. It shall reduce bandwidth consumption by managing the communication protocol of Kantech controllers at the remote site. Polling of Kantech controllers shall be done by the Kantech IP Link or KT-400 in the field and not over the network. The Kantech IP Link or KT-400 shall provide support for up to 32 door controllers. The Kantech IP Link or KT-400 shall be configured from the access software or from a web page which has the security feature of being disabled after successful use.

- For sites that do not have network links, communication to remote sites shall be ensured by Dial-up modems. This shall only be applicable with the use of Multi-site Gateways. The SMS shall support up to 32 such modems that can simultaneously communicate and transmit or receive data from remote sites. No modem shall be dedicated to specific sites; communication shall be established such that the first site calling shall have access to the first available modem, and so on.

- Each Multi-site Gateway shall be able to control 32 local controller loops by using the RS-232/RS-485 protocols via serial or USB port. In addition, each Multi-site Gateway shall be able to control up to 512 Ethernet loops using TCP or UDP protocols, via the use of the Kantech IP Link, or KT-400 of 32 controllers each.

- In all communication methods, the door controller shall retain in their memory all necessary data for controlling doors that they supervise. In case of communication failure, the door controller shall execute all its functions normally.

- 2.4	PERFORMANCE – PROGRAMMING & CONFIGURATION

- 2.4.A	User Section

- This section shall include all functions involved in the issuance of an access or ID card as well as database search and importation tools. During the addition or modification of a card, information about the card shall be sent to the door controllers affected by these new parameters as soon as the operator accepts the addition or modification. An additional command requiring a reloading of the cards database in the door controllers shall not be acceptable.

- The SMS shall allow adding door access exceptions to the cardholder’s list of access rights.

  - The SMS operator shall be able to provide a pre-defined access level and separately add a specific door to be part of the cardholder’s access rights.

  - The door shall have its own schedule.

  - The SMS operator shall have the option of allowing or disallowing access to that door based on that schedule.

  - There shall be no limit to the number of doors that can have exceptions.

  - The KT-400 shall keep in memory the door access exceptions even in standalone mode.

- The SMS shall enable the creation and definition of a user access card. There can be up to five cards per user and users can be managed by cardholder name or card number. When creating user cards, the operator shall be able to select a card format directly from a Card dialog and enter the card number as it is printed on the card.

- The following user information shall be able to be saved in the user section:

  - 5 card numbers each with their own expiration date, trace and lost or stolen statuses.

  - First and last name.

  - Card type.

  - Additional information (10 fields).

  - Start date.

  - Expiry date.

  - Personal ID number (PIN).

  - State of the card.

  - Multi-swipe activation.

  - Comments.

In addition, it shall be possible to associate a photograph, signature, and badge template to a card.  The picture of the card holder shall always be visible when the profile is active on the screen.

5.	The SMS shall allow for the creation of an unlimited number of card templates to be used as ID cards. Template parameters include name, number of sides, and size. It shall be possible to directly print a template on an access card. The operator shall be able to design customized badging templates directly from the access management software. No specific badging program or software other than the latter and no additional licensing shall be required for this function. Any workstation shall be capable of creating ID cards based on operator security level. The following items shall be capable of being added to and modified on a badge template:

  - All information fields associated to a cardholder.

  - Bar code.

  - Text zone.

  - Start date, expiry date, today’s date.

  - Saved images and logos.

  - Borders.

  - Rectangles (including rounded rectangles, ellipse).

  - Lines and arrows.

  - Photograph (can be cropped).

  - A background.

- The SMS shall allow for the creation of a day pass to be issued to visitors for a single day. The SMS shall also have the ability to create temporary ID visitor cards.

- The SMS shall offer the possibility of modifying the parameters of a group of cards simultaneously based on Card Type. The system shall enable the creation of an unlimited number of card types. The following fields shall be modifiable:

      - Card status (valid, invalid, lost, stolen).

      - Card monitored (yes, no).

      - Start date (schedule).

      - End date (schedule).

      - Delete after expiration (yes, no).

      - Wait on keypad (yes, no).

      - Access group (selection menu).

      - Template model (selection menu).

- The operator shall be able to search for a card by last or first name, card creation date, card number, or any of the ten fields of user definable information. The system shall display the last card transactions, namely the latest sixteen denied access events, authorized events, database events, and/or time & attendance events.

- The operator shall be able to quickly view the cardholder’s door list

- Operators shall be able to export the door access list.

- A detailed view of the door’s schedule shall be show when selecting a door.

- The operator shall have the option of expanding the comments field in the user section for better viewing.

- The SMS shall enable the creation of an unlimited number of Import/Export models, give them a name, select required fields, select their layout, and determine the filed delimiter. This shall allow for acceleration of the data entry process by importing databases from a spreadsheet.

- The SMS shall allow for 250 access levels programmed per loop/site of controllers. Every card shall be assigned an access level which shall determine where and when the access card will be valid. When the system consists of several sites or gateways, it shall be possible to use batch programming of access levels.

- The SMS shall allow for creation of tenant lists that can be imported in the (Kantech Telephone Entry System) KTES units. The lists shall be easy to fill up and allow for up to 3000 tenants in each list. The SMS shall support the creation of unlimited amounts of tenant lists.

- The SMS shall allow of importing and exporting of tenant lists.  The operator shall have the ability to choose which fields to import and export.

- The following tenant information shall be able to be saved for each tenant.

      - Tenant name.

      - Tenant ID (customizable in length per tenant list).

      - Primary Telephone Number.

      - Secondary Telephone number.

      - Tenant PIN (customizable in length per tenant list).

      - Pin access schedule.

      - Tenant level.

      - Tenant language.

      - Card number.

      - Disable card trace.

      - Start/End date.

      - No disturb schedule.

      - Prioritized tenant in the display list.

      - Call second phone number option schedule.

        - Ability to call the second phone number only (does not call primary) during valid schedule.

- The SMS shall allow for a card number to be assigned to specific tenant. The KTES unit will be able to send the card number to other controllers of a Wiegand protocol.

- The SMS shall allow for an unlimited amount of Card Types. Cards types shall be used to group cards together for ease of management.  Card types shall have the option of being assigned a card access group template.  Card access groups shall be copied to the card holder profile to give the card holder’s access levels.

- The SMS shall provide the possibility to perform card batch operations. The mass card modifications shall take effect in real time. Each batch operation shall allow for mass cards to be changed based on their card type.  The batch card modification shall be able to change:

  - Card State.

  - Supervisor level.

  - Card count value.

  - Card Tracing.

  - Start Date.

  - End Date.

  - With deletion on expiration.

  - Waiting for keypad.

  - Card access group.

  - Replacing access levels.

  - Updating access levels.

  - Adding new access levels.

  - Updating and adding new access levels.

  - Card Badge layout.

- 2.4.B	Video Section

- The SMS shall be capable of being combined with up to 128 American Dynamics Intellex digital video recorders and American Dynamics Hybrid DVR (HDVR), American Dynamics TVR2 and American Dynamics Video Edge NVR v4.00 without any additional licensing.

- The SMS shall be combinable with up to 128 Panasonic DVR/NVR with a valid option code.  The SMS shall support the following Panasonic DVR/NVR:

  - WJ-ND400

  - WJ-ND200

  - WJ-ND300A

  - WJ-HD220

  - WJ-HD309A

  - WJ-HD316A

  - WJ-HD616/WJ-HD716

  - WJ NV200

- From any of the workstations it shall be possible to do the following:

  - View one or more camera images from different sources.

  - Query the history of each recorder and view images saved on disk.

  - View, modify, or delete programming parameters of a recorder.

  - Control the movement of all motion cameras directly with the workstation mouse of the SMS (PTZ control).

  - Export camera images to hard disk and Video Vault (capable of exporting multiple formats, password protected to protect chain of evidence).

- The SMS shall ensure the time management and synchronization for all the American Dynamics DVR/NVR. It shall be possible to determine the time refresh frequency on the network for the American Dynamics DVR/NVR. The SMS shall allow for configuration of each DVR/NVR. For each recorder it shall be possible to:

  - Assign a name.

  - Determine the recorder type.

  - Determine the network IP address or domain name (DNS).

  - Manually configure the video, communication and event ports.

  - Determine the number of cameras.

  - Determine the query frequency.

  - Determine the number of failed queries required before a loss of communication message is displayed on the screen.

  - Import camera details from existing video servers.

- The SMS shall define the programming parameters for every camera connected to a DVR/NVR. For each camera it shall be possible to:

  - Assign a name.

  - Determine the type of camera.

  - Assign a representative icon for identification on a graphic screen.

  - Determine if the camera image can be visible on a video view.

  - Determine the type of recording.

  - Determine which events from the recorder shall display an alarm message on the screen.

  - Determine the number of pre-selections desired.

  - Determine the number of patterns desired.

  - Add comments to record in the Video Vault.

- The SMS shall allow for the creation of an unlimited number of video views. For each video view it shall be possible to connect up to 16 cameras from various sources.

- The SMS shall be able to incorporate on the same view multiple cameras from different American Dynamics Intellex DVRs or graphics.  Furthermore on different video views the SMS shall be able to incorporate multiple cameras source from different American Dynamics HDVR or graphics.  In addition on different video views the SMS shall be able to incorporate multiple cameras source from different American Dynamics TVR2 or graphics.   In addition on different video views the SMS shall be able to incorporate multiple cameras source from different American Dynamics Video Edge NVR or graphics. Also, on different video views shall the SMS be able to incorporate multiple camera sources from different Panasonic DVR/NVR of the same model or graphics.

- The video view programming parameters make it possible to:

  - Assign a name.

  - Determine the view size.

  - Determine the refresh rate of the image.

  - Determine whether to show metrics.

  - Determine whether to show camera controls.

  - Determine whether to show overlays.

  - Determine whether to auto-hide text.

  - Determine whether to activate image zoom.

  - Determine whether to activate video sequence.

  - Determine delay before sequence launch.

  - Determine camera display delay.

  - Determine display pre-selection delay.

  - Determine pattern display delay.

  - Determine graphic display delay.

  - Determine display mode (1x1, 2x2, 3x3 and 4x4).

  - Incorporate up to 16 cameras from various sources or 16 graphics.

- The SMS shall be able to trigger, from one or more specific events, the start of a recording on a recorder with one or more cameras connected to it. The SMS shall allow for the creation of an unlimited number of video triggers. The SMS shall allow for the creation of an unlimited number of recording parameters. For each recording parameter it shall be possible to:

- Define a name.

- Select the DVR/NVR to which this recording parameter refers.

- Select the camera to which this recording parameter refers.

- Associate a pre-selection or size.

- Determine the start recording trigger.

- Determine the pre-alarm time.

- Determine the total recording time.

- Determine the stop recording trigger.

- It shall be possible for a video event on one DVR/NVR to trigger an action on another DVR/NVR.

- The SMS shall allow the playback of all recordings stored on the hard drive of any of the DVR/NVR. The operator shall be able to save the video into the Video Vault.

- The SMS shall provide the operator access to the complete list of normal and abnormal events that required the activation of video recording. The sequence of images can be saved to a hard drive for subsequent consultation and shall be encrypted. The SMS shall allow the operator to access a complete list of alarm recordings in progress including origin of the alarm. The SMS shall be capable of displaying a list of exported videos.

- It shall be possible to view recorded video tagged to an Access or Video event by quick linking from the Message desktop.

- The SMS shall be capable of connecting 128 American Dynamics DVR/NVR with no additional options needed.

- The SMS shall allow increasing the number of American Dynamic DVR/NVR in groups of 128 by the use of option codes.  The SMS shall support unlimited connections.

- The SMS shall allow for installation of remote modular video managers.  The remote video managers shall be available only after the first 128 connections have been reached,

- 2.4.C	Definition Section

- The SMS shall allow the creation of 100 schedules per loop/site of controllers and an unlimited number of system schedules. Each schedule can include up to 4 intervals. A schedule can be associated with a supervision point, a relay, an access level, a door, elevator floor, an operator, or an event. The SMS shall allow time zone management.

- With a Multi-Site Gateway, specific schedules which include up to 20 intervals shall be available for the KT-400.  The KT-400 shall keep all 20 intervals in memory when in standalone mode.

- The SMS shall allow the creation of 366 holidays. It shall be possible to define a name, define a date, and determine the type. The SMS shall allow the operator to view all the holidays defined in holiday type and sites by viewing them all in a yearly calendar.

- The SMS shall not require for a same date to be created multiple times when affecting certain sites.  The SMS shall allow for the same holiday date to be used on certain sites or on the entire system.

- The SMS graphics shall enable operators to view the exact location of a component installed at the site, or the state of components and peripherals represented in the graphic such as doors, contacts, motion sensors, controllers, video views and cameras. The SMS shall allow for the creation of an unlimited number of graphics. The components on the graphics represented by icons as well as the graphics themselves shall have the ability to be modified.  The SMS shall allow for printing of the graphics with their respective components on the graphical floor plan.

- The SMS shall allow the management of 2,048 elevator cabs of 64 floors each for each gateway. It shall be possible to associate a schedule to the call button. Outside of the schedule, a valid card for a particular floor will have to be presented to the cab reader for it to be activated. The floor selection button group associated with the card’s access level will become operational for a predefined duration and all other buttons shall become inactive. The SMS shall allow the creation of groups of floors and access levels.

- The SMS shall provide the possibility to setup unlimited amount of tasks via the user friendly Task Builder. The operator shall be able to create email templates that can incorporate variable to dynamically populate the emails. Using the command GUI menu, the operator can program commands for any component in the SMS. Commands such as but not limited to lock, unlock, temporary unlock, toggle, back to schedule for the doors, relays, inputs and enable and disable readers. The operator can also program commands for specific card count. The commands shall be able to accept specific components or variables that can filled dynamically.

- The SMS shall provide the possibility to setup unlimited batch card operations via the user friendly Task Builder.  The batch card modifications shall take effect in real time. Each batch card modifications task shall allow for cards to be changed based on their card type.  The batch card modification task shall be able to change:

        - Card state.

        - Supervisor level.

        - Card count value.

        - Card tracing.

        - Start date.

        - End date.

          - With deletion on expiration.

        - Waiting for keypad.

        - Card access group.

          - Replacing access levels.

          - Updating access levels.

          - Adding new access levels.

          - Updating and adding new access levels.

        - Card badge layout.

- The SMS shall provide the possibility to assign the tasks previously created to be triggered on specific components and specific events.

- The SmartLink Task Commander shall process the command from the first available SmartLink application on the SMS.

        - The use of a specific SmartLink to run the SmartLink Task Commander shall not be accepted. The SMS shall accept multiple SmartLinks to be installed thus providing a redundant SmartLink for all SmartLink Task Commander tasks.

- 2.4.D	Devices Section

- The physical components of the SMS including workstations, Multi-site gateways, gateway, site, controllers, Kantech Telephone Entry System (KTES), doors, relays, and monitored inputs shall be individually configured and defined. Individual sites shall also be defined. The software shall allow the use of a controller Express Setup feature in order to minimize the time needed for controller definition.

- Each component in the Devices Section shall allow for a comment section per component.  The SMS shall allow for unlimited amount of characters in the comment section.

- 2.4.E	Alarm Interface

1.	The SMS shall interface with any external alarm system thereby arming or disarming the system by presenting a valid card to an entry / exit door. It also shall be possible to associate a keypad with a reader forcing the cardholder to enter a number in the keypad after presenting a card. This integration shall only be possible with the use of a Multi-site gateway. It shall be possible at a minimum to:

  - Set a monitored input as an arming button.

  - Associate a usage schedule with an arming button.

  - Set the exit and entry delay.

  - Determine whether the system must wait for a valid access to arm.

  - Determine whether the system must wait for a valid access card swipe and appropriate pin number to disarm. Determine whether the door must relock on arming request.

  - Associate a monitored input with an alarm panel condition.

  - Lock a door unlocked by a schedule when armed.

- 2.4 F 	Intrusion Integration

    - The SMS shall allow interface with the DSC PowerSeries PC1616, PC1832, PC1864 and MAXSYS 4020 series alarm panels intrusion panel thereby eliminating hardwired integration between the SMS controllers and the DSC PowerSeries® intrusion panel.   The DSC PowerSeries® intrusion panel shall communicate with the Multi-site gateway via RS-232 or directly to a KT-400 controller.  The SMS shall allow for:

- Single/multiple partitions arming and disarming via reader.

          - Disarm via card only or forced valid card and pin.

- Single/multiple partitions arming and disarming via operator commands.

- Receive events from intrusion panel.

- Receive partition names, user codes and zone names programming.

- Update user codes.

- Assign user codes to cardholders.

- Viewing a fully functional virtual keypad to perform all functions available on the DSC PowerSeries® or the MAXSYS 4020 intrusion panel keypad.

- With the MAXSYS 4020 integration the SMS shall be able to control the PGM outputs from a graphic screen.

- 2.4.G	System Section

- The SMS shall define the profile of a system operator based on name, password, language, privileges, login schedule, security level, workspaces, and password expiry date. The SMS shall provide the possibility to force the operators to assign a mandatory card type to the users. The operator shall be able to provide a default card type for every card.

- The SMS shall determine access rights granted to an operator based on security levels. There shall be three predefined access levels called Installer, Administrator, and Guard.  The SMS shall have the ability to create an unlimited number of security levels that can be assigned to one or more operators. It shall be possible to determine from which system components the operator shall be authorized to receive events and take action.  It shall be possible to specify for each programming window if the operator can (any combination):

  - View the component in read only.

  - Add new components.

  - Modify existing components (cannot add new).

  - Delete components.

  - Save as.

  - Print components.

  - View links.

- The SMS shall allow System Administrators to grant or deny operators access to all system physical components such as gateways, sites, controllers, doors, relays, inputs, access levels, reports, schedules, tenant lists, video servers, card types, etc. using Workspaces. This allows greater ease for larger sites to locate and assign components that pertain to specific gateways and sites. System administrators shall be able to tailor specific system applications and workstations Workspaces, therefore restricting access to information to all levels of operators. Operators shall be able to use temporary workspaces to narrow their fields of view when accomplishing specific tasks, and then easily revert back to their main workspace.

- The SMS shall allow for the creation of unlimited instructions. These instructions shall be attributed to one or more events that will be used in documenting the event and guide the operator on duty in performing tasks. It shall be possible to edit the instructions in two different languages.

- The SMS shall make it possible to customize system events. All events shall be pre-defined to display on all system workstations. For each event it shall be possible to:

  - Determine a display schedule.

  - Determine a color.

  - Assign a printer.

  - Associate one or more workstations.

  - Associate an instruction.

  - Associate a schedule for an acknowledgement request.

  - Determine the priority level.

- 2.4.H	Report Section

- The SMS shall include templates for various types of reports to include the following:

  - Card use reports.

  - Manual operations reports.

  - Alarm reports.

  - Historical reports.

  - Time & Attendance reports.

  - Detailed reports.

  - Summary reports.

  - Statistical reports.

  - Roll Call Reports.

    - The SMS shall allow for the creation of custom reports based on any event or component in the system. The SMS shall support an unlimited amount of customized reports.

    - All reports shall be able to be displayed on screen, printed, or sent by e-mail on a daily, weekly, or monthly basis. All event reports can be automated to be generated and sent at a specific time for a specific time period.

    - The SMS shall support at a minimum the following report formats: Sybase, Dbase IV, CSV, XLS, PDF, RTF, and TXT.

    - The SMS shall be able to generate an access report in CSV with all the card information associated to that access event.

    - All component modification events shall be tagged with addition (+), modification (=) or deletion (-) tag.  In all event driven reports the operator shall have the choice to specify a tag or all tags in order to further filter report.

    - The system shall support for the creation of custom Time and Attendance reports. Each time and attendance report shall support up to 32 rules for masking the entry and exit times of each card. Also each report shall support a “First entry and last exit” feature.

    - Time and attendance reports shall have the possibility to compile the report in using fractions base (percentage) or actual hours and minute base.

    - The SMS shall allow the creation of custom Roll Call reports, which can without operator intervention be emailed to multiple people and/or printed on multiple printers. The Roll Call report shall be a system wide feature.

    - Each report, quick report, historical report and time attendance report shall have a priority number assigned to it. When multiple reports are requested.  The SMS shall prioritize the creation of the report based on their priority number.  From the Report queue management window the operator shall have the possibility to promote the report to a higher priority.  The operator shall also have the ability to request more processing power form the computer in order to expedite the report creation.

    - Reports shall be prioritized from queue of 1 to 99.   When the report is requested as priority 1 it shall be processed first. The default value for all new reports shall be set to 50.  Operators shall be able to change it as needed.

- 2.4.I	Help Section

- The SMS shall have contextual help button every window.  The operators shall also have option of pressing F1 on their keyboard and Help window will appear with the correct section of the item they were looking at in the SMS.

- The SMS shall include an About window which shall include basic information about the SMS.  It shall also include the KAP start/end date and tokens needed.  The operator shall be able to send KAP details via email to a pre-defined email list by the click of one button.

- In addition the About Window shall include contact information for the SMS manufacturer and contact information for the installation company/dealer.  The dealer information shall at a minimum but not limited to:

- Company name.

- Address.

- Website link.

- Email link.

- 2.4.J	Options Section

- The SMS shall allow operators to access basic server and display functions and allow the operator to determine default settings for the server hard drive. The operator shall also be able to determine the time to perform a server backup, programmable on monthly, weekly, or daily basis.  It shall be possible to schedule and plan mass automatic KT-400 firmware updates.

- The SMS shall allow for the servicing company to enter their contact information for the SMS operator’s disposal.

- 2.4.K	System Status Section

- The SMS shall allow operators to view the state of various access system components in text or numerical form. A specific controller’s state shall also be able to be viewed in graphic form via the picture of the controller with the status of each terminal. Workstation and database status shall also be able to be displayed.

- 2.4.L	Various Tools

- The SMS shall employ an Express Setup to configure system components such as sites and controllers, as well as peripherals associated to these components such as ports and inputs. This utility will reduce the programming time to a minimum.

- The SMS shall employ a database utility to allow the re-indexation and verification of archived files and verify the integrity of indexes, links, and database arborescence.

- The KT-Finder tool shall help troubleshoot the Kantech IP Link and KT-400 on site or remotely. It can also be used as an alternate method of configuration for both.

- The SMS shall include a vocabulary editor to be used in designing custom language dictionaries.

- 2.4.M	Video Vault

1.	Video Vault is an optional remote networked application used to automate recovery of video data from the DVR/NVR and save it on a disk for long term video storage and retrieval. The information can be stored on an independent system or within the server. The footage that shall be tagged and recoverable from the DVR/NVR shall include SMS triggers, manual triggers, and saved video server footage.

2.	For the archived video files it shall be possible to:

- Assign a folder name to index the archived files.

- Create sub folders based on day of the week, day, week, month of the year, month, video server name, camera name and/or event description name.

- Determine the hard drive to store the recovered videos.

- Determine the composition of the name of the saved file.

- Determine the format of the saved video.

- Assign a frame from the saved video to represent as a saved file.

- Determine the number of simultaneous downloads.

- Determine a size limit for recoverable videos.

- Assign a password to videos stored.

- Determine a delay between requests to the server.

    - There shall be scheduled transfers for archiving thereby reducing video network traffic during peak times.

- 2.5	PERFORMANCE – EntraPass Web / MOBILE APP

- 2.5.A	EntraPass Web

- EntraPass Web shall be an optional tool that will allow for performing certain functions from a remote location to be used with the regular SMS system via a Web browser.

- EntraPass shall be Silverlight based and be a download application from the main web server.  The operator shall simply have to run the EntraPass Web from their Desktop.

- EntraPass Web shall be automatically updated when the main web server is updated.

  - Manual updating of EntraPass Web shall not be supported.

- EntraPass Web shall offer the following operations:

  - Operator specific security rights.  The SMS workstation shall allow configuring operators to be able to access EntraPass Web.  It shall also allow the operator’s security rights and workspaces to be used on the EntraPass Web.  An operator who cannot add cards on the SMS workstation shall not be able to do the same on EntraPass Web.

  - Automatically adjust the operator’s language selection.  The language selection shall be done at the creation of the operation in the SMS workstation. The languages supported shall be English, French, Spanish, Italian, Portuguese, Simplified Chinese, Dutch, Turkish and German.

  - There shall be no limits to the amount of EntraPass Web that can be installed.

  - Shall not require any kind of refreshing to receive any new data

    - Refreshing the “page” shall not be supported.

  - EntraPass Web licenses shall be managed by concurrent active logged on sessions.

    - The need to have dedicated licenses per computer shall not be supported.

  - Shall support right-clicking to allow additional functions.

  - Shall include onscreen overlay tutorials to help guide the operator on how to use the user, access level, holiday, tenant, schedule, Dockview windows and others.

    - The tutorials shall be simple, easy and straight to the point.  The tutorial overlay shall fade out when the operator actively moves in the screen.

    - The tutorials shall have the ability to be turned off if no longer needed.

  - Shall include context-sensitive help in a separate window to provide complete help on specific topics.

- EntraPass Web shall have a complete, easy to use and intuitive look and feel.

- EntraPass Web shall provide complete card management.

  - EntraPass Web shall learn and remember the operator’s screen settings.

    - It shall be possible to see all settings of the cardholder at once without the need to use tabs.

    - Its fields shall be grouped in a logical order to allow operator to completely accomplish their tasks without moving around the window.

  - EntraPass Web shall allow configuring every aspect of the card that the EntraPass Workstation offers.

  - EntraPass Web shall include the additional operations for the card holder:

    - Link a cardholder to a tenant list for the KTES;

    - Import and take a picture of the cardholder using a web cam;

    - View a list of cardholders in a list;

    - The cardholder list shall be configurable to include cardholder information.  It shall also allow to sort by columns;

    - The cardholder list shall allow for a right click function to modify or delete the cardholder;

    - Search by card number and username;

    - Import and export cardholders via CSV;

- EntraPass Web shall provide complete access level management.

  - EntraPass Web shall allow the operator to customize their access level list to show more access levels in columns in order to provide a better view of the access levels.

  - EntraPass Web shall provide a preview on how the access level is programmed:

    - It shall be possible to zoom in the access level preview and see down to the hour how the access level is programmed.

- EntraPass Web shall provide complete schedule management.

  - EntraPass Web shall allow the operator to customize their schedule list to show more schedule in columns in order to provide a better view of schedule.

  - EntraPass Web shall provide a preview on how the schedule is programmed

    - It shall be possible to quickly program the schedule by either entering the times or using a scroll bar.

    - It shall also be possible to quickly program the days by choosing them manually or selecting pre-defined day templates.

- EntraPass Web shall provide complete holiday management.

  - EntraPass Web shall allow the operator to customize their holiday list to show more holidays in columns in order to provide a better view of holiday.

  - EntraPass Web shall provide a preview on how the holiday is programmed.

    - It shall be possible to program the holiday date and using the drag and drop function to select the appropriate sites affected.

- EntraPass Web shall provide complete tenant and tenant list management.

  - EntraPass Web shall allow the operator to customize their tenant list to show more tenant lists in columns in order to provide a better view of tenant lists.

  - EntraPass Web shall allow for complete tenant programming in an easy to use GUI interface.

  - It shall be possible to see all tenant settings at once without the need to use tabs.

- EntraPass Web shall allow for map management.

  - The operator shall be able to easily and intuitively use the map creation tool to import floor plans or maps in EntraPass Web.  The image formats support shall be JPEG and GIF.

  - The operator shall have the ability to place components on specific parts of the map and assign double click actions.

  - The operator shall be able to view maps from their screen.

  - The operator shall be able to:

    - See real time visual status of a component.  At a minimum the following components shall be available:

      - Doors and elevators

      - Inputs

      - Relays

      - Map links

      - Virtual keypad

      - Controller

      - Video Cameras

    - Double click on the component to perform actions.

    - Right click on the component and choose a different action

    - Quickly move to different maps without  by using links

    - Maximize the map.  The EntraPass web shall be able to keep the visual aspect ratio.

  - The operator shall be able to modify the assigned door schedule from the map

    - The operator shall not need to have access to entire door to be able to change the assigned door schedule

    - Changing the door schedule shall be a privilege that can be turned on or off by the SMS administrator per operator

- EntraPass Web shall provide video integration with the American Dynamics HDVR and Video Edge (NVR) products.

  - EntraPass Web shall allow the operator:

    - To create and manage video views

    - To select a single camera and drag it into the viewing screen to view live video.

    - To select a predefined video view and drag it into the viewing screen to view live video.

    - To view video cameras without the need to create video views.

    - To select 9 different video camera layouts.

    - To support up to 16 cameras at once per view.

- EntraPass Web shall allow the operator to view events in real time.

  - EntraPass Web shall allow the operator:

    - To view events in real time.  Each event at a minimum shall include:

      - Date and time

      - Event name

      - Description of the component

  - The event viewer shall support natively a swipe and show feature.  The picture of cardholders shall appear on access related events.

  - On predefined video alarm recordings, a video button shall appear on the event screen for each event that has video alarm.

    - The operator shall be able to click the button to view the alarm video clip.

  - From the Event viewer the operator shall be able at a minimum to:

    - Search for any event, date, time, description using the Filter field

    - Sort by Date/time, Event and Description.

- EntraPass Web shall allow for the DSC Virtual keypad to be used.  From the maps the operator shall easily be able to bring up a fully functional DSC Virtual keypad and perform all actions allowed by the DSC PowerSeries 1616, 1832, 1864 keypad.

- EntraPass Web shall allow for the programming of Kantech hardware.

  - EntraPass Web shall support but not be limited to programming the following:

    - IP sites

      - IP link

      - KT-400 IP

      - KTES IP

    - Direct sites

      - USB or Serial

    - Controllers:

      - KTES

      - KT-100

      - KT-200

      - KT-300

      - KT-400

    - Component

      - Door programming including but not limited to:

        - Multi-swipe settings,

        - Intrusion arming/disarming

        - Unlock/open settings

        - Door contact and Rex settings

        - Schedule assigned

        - Door naming

      - Relay programming including but not limited to:

        - Activation schedule

        - Disable relay schedule

        - Temporary activation timer

        - Relay naming

      - Input programming including but not limited to:

        - Monitoring schedule

        - NC/NO status

        - Relay activation settings

        - Input Name

  - EntraPass Web shall support a quick, intuitive and easy to use express setup to configure controllers and their doors, relays and inputs.

  - The operator shall be able to modify, delete or add components manually after the express setup.

  - The operator shall be able, at a glance, to see in a visual and easy to understand the site communication time, communication status and the number of controllers communicating.

    - The operator shall also be able to see the communication status per controller.

- EntraPass Web shall provide email notification and alarm management with the Watchlist.

  - EntraPass Web shall have the ability to manually select which door, relay, input and elevator will be watched for abnormal events.

  - A watched component shall generate an alarm on EntraPass Web. The operator shall have a time ticker (Watchlist) where all the alarms will appear as small colored circles.

    - Each event shall be categorized with the appropriate color by the SMS.

  - The operator shall be able to:

    - Highlight the event and see more information that shall appear.

    - Right click on the event and go to associated:

      - Component

      - Video recording

      - Map

    - Scroll back to the first alarm since he logged in to an EntraPass Web session.

    - Shall be able to tag a Watchlist with email notification as well.

- EntraPass Web shall provide Dockviews.

  - The operator shall be able to create unlimited amount of Dockviews.

  - Each Dockview shall be customizable to the operator’s specifications.  A Dockview can be customized to have any but not limited to the following items:

    - Naming the Dockview

    - Schedule Management

    - Access Level Management

    - Holiday Management

    - User Management

    - Tenant Management

    - Door/Elevator Operations

    - Relay Operations

    - Input Operations

    - Events

    - Maps

    - Video Viewing

    - Reports

  - Each Dockview shall have the ability to:

    - Pin as favorites

    - Make floating views usable on multiple screens embedded in EntraPass Web

    - Assign to various operators

  - The operator shall have the ability to open an unlimited number of Dockviews at the same time when they are setup as floating views.

- EntraPass Web shall at a minimum be supported by any web browser and Windows® OS supporting Microsoft® Silverlight plug-in.

- 2.5.B	Mobile APP

- Mobile App is an optional tool that will allow performing certain functions from a remote location to be used with the regular SMS system via iPad, iPhone, Android phones and Android tablets. The Mobile App provides card management to guards, secretaries, or managers without the need to deploy a full workstation. A concurrent connection option shall provide access to a predetermined number of simultaneous users.

- The concurrent connections are shared with the EntraPass Web connections.

- The Mobile App shall have the ability to be viewed in multiple languages. The Mobile App shall be available in English, French, Spanish, Italian, Portuguese, Simplified Chinese, Dutch Turkish and German. The languages shall be preselected based on the device language.

- The following functions are available using Mobile App:

- Card management (including 5 cards per username).

- Live card holder picture capture using a camera.

- Creating, modifying and deleting access levels.

- Creating, modifying and deleting schedules.

- Assigning access levels.

- Performing door operations.

- Performing relay operations.

- Performing input operations.

- Performing elevator operations.

- Requesting historical reports via email.

- Viewing live events using the menu or the quick launch viewer.

- Search for events using text filters.

- The Mobile App shall support multiple SMS logins and servers stored in memory.

- The SMS shall support gesture logins in order to login securely and quickly to the Mobile App.

- The Mobile App shall be downloadable at no-charge from the App Store® and Google Play®.

- The Mobile App shall be supported but not limited to:

  - Apple:

    - IPhone, iPod: 3GS, 4, 4S, 5

    - iOS: 4, 5, 6

  - Android:

    - Galaxy S2, Galaxy Nexus

    - Nexus One, Nexus S

    - OS:

      - Ice Cream Sandwich

      - Jelly Bean

- 2.6	INTEGRATION

- 2.6.A	SmartLink

- The SmartLink application offers the ability to send messages to pagers and cell phones and through the use of e-mail. SmartLink provided instant e-mail notification of alarm events and the ability to e-mail reports.

- Integration with other systems can also be done through the SmartLink API. This tool is used for advanced integration with third party applications like visitor management software, human resources systems, time and attendance systems, video systems, HVAC, etc.

- 2.6.B	Card Gateway

- The Card Gateway is an optional external interface that shall allow the client to make modifications to the system card database through an Oracle or MS-SQL database. The application may be installed and run on the server’s CPU. It shall allow for HR software integration and enable operators to modify, add, or obtain information on cards in real time.

- 2.7	REDUNDANCY & MIRRORING

- 2.7.A	Redundant Server

- The SMS shall be able to support an optional redundant server whose main function shall be to monitor the primary server and ensure automatic (Hot Standby) take over if necessary. The redundant server shall have all the same characteristics and functions as the primary server.

- The transition between these servers shall be completely transparent. When the primary server is operational once more, it shall be capable of synchronizing its database automatically with the redundant server and then resume absolute control of the access management system. No human intervention shall be required in this operation.

- The operator shall be able to perform any and all operations during a fail-over synchronization between the primary server and redundant server.

- The system shall support the use of multiple simultaneous redundant servers. The need to install third party (not EntraPass) licensing shall not be acceptable.

- 2.8	SOFTWARE AUTO-UPDATER

- The SMS shall allow for SMS applications to be automatically updated to the latest version when then SMS Server is updated to a newer version.

- Each SMS application shall have the option of being configured to react differently during an update.  Each SMS application shall have the option of:

  - Manual.

    - The SMS application shall be updated manually on the local computer.

  - Automatic.

    - The SMS applications shall all be updated automatically when the applications are connected to the SMS server.

  - Queued.

    - The SMS Server shall update one application at a time.

  - Prompt to download.

    - The SMS workstation shall be prompted to be updated.

- The need to copy the installation package shall not require being physically on SMS applications that require updating.

- The SMS v5.02 or higher can be updated automatically to newer versions.

- 2.9	HSPD-12 COMPLIANCE AND INTEGRATION

- The SMS shall be HSPD-12 compliant when integrating with PIVCheck Plus and Certificate Manager Solution.  The SMS and PIVCheck integration shall be seamless and the operator shall not need to enter the cardholder’s information twice.

- The integration shall support up to three-factor authentication, extraction and verification of the cardholder’s data on the FIPS 201 smart card and shall perform a biometric match against the template stored on the card. Digital certificates shall verify against the issuer’s validation authority, SCVP or OCSP Responders.  All cards shall be validated using the FIPS 201 challenge-response (CAK or PAK) in order to identify forged or cloned cards.  The SMS integration shall work with all PIV, TWIC, CAC and FRAC cards.

- The PIVCheck solution shall verify the following items to ensure that the cardholder is the card owner, the card is authentic, and the card has not been revoked by the agency that issued it:

  - Smart card expiration date.

  - Non-duplicated card (forged/cloned).

  - Biometric.

  - Certification status.

  - PIN verification.

- The SMS shall natively support the FIPS 201 driver when using the KT-400 controllers and shall display the FIPS 201 card number correctly.

- The SMS integration shall allow associating SMS card fields with the PIVCheck card field in order to have a seamless card holder entry.  The SMS integration shall allow but not limited to associating with the following fields:

- User definable fields (10).

- Card holder pin.

- Card Number.

- Card user name.

- Card type.

- Card status.

- The SMS integration with PIVCheck shall require option codes to activate all integration functions.

- 2.10	OPERATION

The SMS shall perform the following tasks:

- Allow card access management for one or more buildings.

- Control access to various doors equipped with a card reader. Allow the ability to set card use count options to limit the number of times a card can be used.

- Monitor all defined alarm points as well as all doors controlled by card readers based on programmed schedules.

- Send transactions for which printing is required to one or more printers, based on a set schedule.

- Access the system using the main and secondary menus (to which access is limited by a password) to make additions and required changes to various data files so that they can be updated by the user without the manufacturer’s assistance.

- Enable the entry of access code data for every card or group of cards.

- Seamlessly connect to onsite alarm systems.

- Fully functional virtual keypad with DSC® PowerSeries PC1616, PC1832 and PC1864 alarm system in addition with the DSC MAXSYS 4020 alarm panel. The operator shall perform all functions available on a standard keypad with the PowerSeries or MAXSYS 4020 series alarm systems. The operator shall be able to use the computer keyboard or the mouse to perform actions on the virtual keypad.

- Associate to each event a recording schedule for each destination (hard drive, monitor).

- Automatically display all alarms on screen in text with optional graphic or picture and trigger a sound requiring an acknowledgement on the keyboard to stop the alarm.

- Alarm pop-ups can be sent to many workstations. An alarm pop-up shall be acknowledged once by one operator.

- Mandatory comments can be added by the operator when acknowledging the alarm pop-up.

- In the case of an unacknowledged alarm within a customizable time; the alarm shall be sent to all active operators with additional log information.

- Each event shall print on a log printer. For security reasons, each event shall be incremented with a print number. Numbering shall start from 0 every day.

- Generate reports and view them on the screen, output them to a printer, or send them to an email address.

- Supervise based on programmed schedules of specific points such as door contacts, volumetric detectors, mechanical points, high and low temperature sensors, or any other equipment necessary for good building management.

- View and/or save video images.

- When integrated into a DVR/NVR system (American Dynamics or Panasonic), allow the management of the recordings of all the cameras via access system workstations.

- When connected to a DVR/NVR system (American Dynamics or Panasonic), allow the orientation of all PTZ cameras directly using the workstation mouse of the access system.

- The SMS shall offer the option to create 4 digit, 5 digit or 6 digit PIN for the card holders.

- The PIN length shall be defined SMS wide.

- When connected to a digital video recording system (American Dynamics), allow the recovery and storage of selected videos to an independent server.

- Save the database manually or automatically backup following a schedule.

- Uninterrupted backups. The operator shall be able to perform any task during a SMS backup.

- The operator shall be able to perform any and all operations during a fail-over synchronization between the primary server and redundant server.

- The SMS shall remind SMS operators via email and messages (pop-ups) of the SMS KAP status.  The SMS shall have pre-defined reminders set to:

- 60 days before KAP expiration.

- 30 days before KAP expiration.

- Day of KAP expiration.

- 30 days after KAP expiration.

- The SMS KAP reminder shall include but not be limited to SMS serial number tokens needed and SMS Edition.

- When the access control system manages parking lot entry and exit, it shall be possible to set a maximum number of vehicles authorized to simultaneously access the parking area. Once the parking lot is full, the system shall prevent access to any cardholder for as long as a parking space has not become available.

- Allow for a Dual Custody option to add extra security to a door by requesting that two card holders must access the door together.

- It shall be possible to program on a KT-400 controller reader to bypass a door contact on a schedule.  The bypass shall be at the controller level and at the software level.

- It shall be possible to bypass the door contact for Door Forced Events and Door open to long events.  It shall be possible to have the Door open too long be an optional bypass on a door basis.

- Operators shall be able at any time to bypass the door contact manually from the SMS workstation.

- It shall be possible to program on KT-400 controller readers a double and triple switch function:

- It shall be possible to have the multi-swipe function activating a predetermined schedule.

- The double and triple swipes shall be able to be activated on reader simultaneously each with their respective actions.

- The multi-swipe function shall be able to but not limited to:

- Toggle door unlock.

- Unlock door.

- Relock door.

- Temporarily unlock door.

- Activate Relay.

- Temporarily activate relay.

- Arm door partition request when using a Multi-Site gateway.

- Each card holder shall have the option of having the multi-swipe function active.

- A specific event shall be generated for any valid or invalid, double or triple swipes.

- Save events on a hard drive according to required criteria.

- Perform the following operations from all workstations:

- Lock or unlock, one time unlock, return to schedule one door or a group of doors.

- View the last access event on the door.

- Bypass the door contact and keep door locked.

- Temporarily unlock a door using a custom timer for additional door unlocking on KT-400 controller doors.

- Disable and enable readers.

- View custom programmed comments in the component’s Operation section.

- Activate or deactivate a relay or a group of relays.

- Activate or deactivate the recording of one camera or a group of cameras.

- Activate or deactivate a point or a group of points.

- Program or modify one card or a group of cards.

- Assign single door access exception to the card.

- Validate or invalidate one card or a group of cards.

- Change time and date.

- Demand the system state in text or graphic mode.

- Query, create and/or modify data on: Access levels, Schedules and holidays, Access card, Instructions, Reports and log, Doors, Supervision points and relays, Operator levels, and Graphics.

- Ability to use an easy to use system tree view to select the components.

- View which cards are in the roll call sectors.

- View the card’s last known access in the roll call sector.

- Perform the following operations from the SmartLink Task Commander:

- Alarm.

- Disable and enable any reader.

- Lock, unlock, temporary unlock return to schedule, disable enable any elevator and elevator floor.

- Activate, deactivate, temporary activate, toggle and return to schedule of any relay.

- Shunt, unshunt, temporary shunt, toggle, return to schedule and continuous supervision of any input.

- Set count usage, manually overwrite the count, disable count usage, decrement count usage, increment count usage for all the cards.

- Send alarm emails.

- The use of variables in the SmartLink Task Commander can be used instead of hard coded values.

- Mass card modifications on without operator intervention.

- Ability to use generically created commands to perform task on different components.

- Each specific card shall have the ability to activate a specific component in the above mentioned states without the need to create hard coded the commands.

- The SmartLink Task Commander shall process the commands on the first available SmartLink on the SMS.

- The use of a specific SmartLink to run a specific SmartLink Task Commander shall not be accepted.

- The SMS all allow for many SmartLinks to be installed without the need to purchase additional option codes.

- The SmartLink Task Commander shall be run from any of the available SmartLink.

- The SmartLink Task Commander shall allow for single or grouping of components of the same type to trigger the same task.  The need to have a specific trigger programmed per component to trigger the same task shall not be accepted.

- 2.12	EQUIPMENT

- 2.12.A	Server and Redundant Server Requirements

The SMS server and redundant server shall meet the following minimum requirements:

- The server shall have a Dual core processor or better

  - If doing video the server shall have an Intel  Quad core processor or better.

- The server shall have a 500-watt power unit.

- The server shall have 4 GB RAM.

  - If doing video, the server shall have 8 GB RAM or more.

- The server shall have 50 GB hard disk drive space.

- The server shall have a 48x CD-ROM drive.

- The server operating system shall be Windows XP Pro 32- bit. Windows 2003 Standard and Enterprise Server Edition, / Windows 2008 Server/Windows 7 / Windows 8. All OS shall be 32-bit or 64-bit.

  - The integration platform requirements shall possibly change the EntraPass requirements depending on integration products.

  - Windows 8 shall support access control functions only.

- The server shall have a 10/100/1000 Base-T network adapter.

- The server shall have a high quality multilingual keyboard.

- The server shall have a two button ergonomic mouse.

- The server shall have an On-Off switch.

- The server shall have an appropriate UPS.

- 2.12.B	Multi-Site Gateway Requirements

The SMS Multi-Site gateway shall meet the following minimum requirements:

- The Multi-Site gateway shall have a Dual core processor or better.

- The Multi-Site gateway shall have a 500-watt power unit.

- The Multi-Site gateway shall have 4 GB RAM.

- The Multi-Site gateway shall have 50 GB hard disk drive space.

- The Multi-Site gateway shall have a 48x CD-ROM drive.

- The server operating system shall be Windows XP Pro 32- bit. Windows 2003 Standard and Enterprise Server Edition, / Windows 2008 Server/Windows 7 /

- Windows 8. All OS shall be 32-bit or 64-bit.

  - Windows 8 shall support access control functions only.

- The Multi-Site gateway shall have a 10/100/1000 Base-T network adapter.

- The Multi-Site gateway shall have a high quality multilingual keyboard.

- The Multi-Site gateway shall have a two button ergonomic mouse.

- The Multi-Site gateway shall have an On-Off switch.

- The Multi-Site gateway shall have an appropriate UPS.

- 2.12.C Workstation Requirements

The SMS workstations shall meet the following minimum requirements:

- The workstation shall have a dual core processor or better.

  - If doing video, the workstation shall have an Intel quad core processor or better.

- The workstation shall have a 500-watt power unit.

- The workstation shall have 4 GB RAM.

  - If doing video, the workstation shall have an 8GB of RAM or more.

- The workstation shall have 20 GB hard disk drive space.

- The workstation shall have a 48x CD-ROM drive.

- The server operating system shall be Windows XP Pro 32- bit. Windows 2003 Standard and Enterprise Server Edition, Windows 2008 Server/ Windows 7 / Windows 8. All OS’s shall be 32-bit or 64-bit.

  - The integration platform requirements shall possibly change the EntraPass requirements depending on integration products.

  - Windows 8 shall support access control functions only.

- The workstation shall have a 10/100/1000 Base-T network adapter.

- The workstation shall have a high quality multilingual keyboard.

- The workstation shall have a two button ergonomic mouse.

- The workstation shall have an On-Off switch.

- The workstation shall have an appropriate UPS.

- 2.12.D	Controllers

The SMS shall support the following door controllers:

- Kantech KT-400:

The KT-400 is an Ethernet-ready four door controller with sixteen monitored points, on-board door strike power, sixteen reader outputs, four relay outputs, and auxiliary power output. It shall accept Wiegand, proximity, ABA clock and data, bar code, magnetic, integrated keypad, and smart card reader types.  It shall also support FIPS 201 cards, with and without checking the expiration date.  It supports RS-232, RS-485 and 128-bit AES Encrypted Ethernet 10/100Base-T communication. It supports expansion modules to provide 256 inputs and 256 outputs.  It shall support 136 double end of line inputs.  It shall support up to support 8 card formats (9 with DUAL ioProx driver).   The KT-400 shall support native 20 intervals per schedule.

- Kantech KT-300:

The KT-300 is a two door controller with eight monitored points on board expandable to sixteen, door strike power, auxiliary power output, and two auxiliary outputs. It shall accept Wiegand, proximity, bar code, magnetic and integrated keypad reader types. It supports RS-232, RS-485, and Combus communication. It supports relay, input, and output expansion modules. The KT-300 is available in 128k and 512k memory versions.

- Kantech KT-100:

The KT-100 is a one door controller with four monitored points, door strike power, and four auxiliary outputs. It shall accept Wiegand, proximity, bar code, magnetic and integrated keypad reader types. It supports RS-485 communication.

- Kantech KT-200 (Legacy).

- 2.12.E	KTES (Kantech Telephone Entry System)

- The KTES enables tenants to grant access to the building, to their visitors, via their own telephone line or cellular telephone. The KTES supports 250 tenants with the option of supporting up to 3000 tenants. The KTES also includes:

- 4 lines x 20 characters LCD module with controllable LED backlighting

- Programming menus available in three (3) languages (English, French and Spanish)

- Built-in RS-485

- 128-bit AES encrypted Ethernet

- Internal modem

- Three (3) relays

- Microphone

- Speaker

- Backup battery

- Optional KTES accessories are:

- Heater kit

- Postal lock

- Color camera

- Goose neck mounting

- Paper index (flush mounted)

- The KTES shall be programmed via the keypad and LCD for stand alone mode or via the SMS.

- The unit shall support a Wiegand reader that will allow tenants to swipe their cards and enter the building.

- The KTES shall employ flashable firmware with auto update.

- 2.12.F	Card and Reader Support

- The SMS shall support configuration of unlimited card formats.

- The SMS shall support up to 2 card formats per KT-100 and KT-300 controller (3 with DUAL ioProx driver).

- The SMS shall support up to 8 card formats per KT-400 controller (9 with DUAL ioProx driver).

- The SMS shall support readers that provide Wiegand signaling and magnetic ABA signaling to include:

  - Kantech ioProx family of readers.

  - Wiegand swipe readers.

  - Proximity readers.

  - Biometric readers.

  - Smart card readers.

  - Wireless readers.

  - Magnetic readers.

- PART III	EXECUTION

- 3.1	TESTING

  - The software shall be entered into the SMS computer systems and debugged. The Contractor shall be responsible for documenting and entering the initial database into the system. The Contractor shall provide the necessary blank forms with instructions to fill-in all the required data information that will make up the database. The database shall then be reviewed by the Contractor and entered into the system. Prior to full operation, a complete demonstration of the computer real-time functions shall be performed. A printed validation log shall be provided as proof of operation for each software application package. In addition, a point utilization report shall be furnished listing each point, the associated programs utilizing that point as an input or output and the programs which that point initiates.

  - Upon satisfactory on-line operation of the system software, the entire installation including all subsystems shall be inspected. The Contractor shall perform all tests, furnish all test equipment and consumable supplies necessary and perform any work as required to establish performance levels for the system in accordance with the specifications. Each device shall be tested as a working component of the completed system. All system controls shall be inspected for proper operation and response.

  - Tests shall demonstrate the response time and display format of each different type of input sensor and output control device. Response time shall be measured with the system functioning at full capacity. Computer operation shall be tested with the complete data file.

  - The Contractor shall maintain a complete log of all inspections and tests. Upon final completion of system tests, a copy of the log records shall be submitted as part of the as-built documentation.

- 3.2	TRAINING

The Contractor shall provide a competent trainer who has extensive experience on the installed systems and in delivering training to provide the instruction. As an alternate, the Contractor may propose the use of factory training personnel and coordinate the number of personnel to be trained.

- 3.3	MAINTENANCE

- The Contractor shall offer a Kantech Advantage Program (KAP) to provide twelve additional months of free software updates and online training for the end user.

- Technical support is available at no charge to all Kantech dealers whether or not they have a KAP activated for the systems they are supporting.

END OF SPECIFICATIONS